How to Use this Form

The purpose of this form is to support the process of confirming that an Approved Design contains all the required information prior to it being submitted for Appraisal.

The options open to the Design Approver are:

- To use this form as a personal checklist that the design documentation contains all the required information prior to Approving the Design, or;

- To include this form as part of the design documentation that is Approved and submitted for Appraisal. In this instance the Design Approver must complete and sign the relevant sections. Non relevant sections should be deleted from the submission.

Contents

1.	Schedule of PS/6 Design Documentation submitted for Appraisal	2

2.	Existing Pressure System Details	3

3.	Design Specifications	4

3.1	Pressure Reduction Installations (Inlet Pressures up to 100 Bar)	5

3.2	< 7 Bar Steel System	9

3.3	< 7 Bar Plastic System	13

3.4	75 mBar – 100 Bar Metering Installation	16

3.5	Cathodic Protection	19

3.6	Civil Works	20

4.	Other items which Appraisals will check	21

4.1	Mechanical / Gas Process Engineering Appraisal	22

4.2	Civil / Structural Appraisal	26

4.3	Safety / Human Factors Appraisal	31

4.4	Cathodic Protection Appraisals	32

# Schedule of PS/6 Design Documentation submitted for Appraisal

| Drawing / Document Reference Number | Revision | Description |  |  | Design Approver Check Box |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Design Approver Name |  |  |
|  |  |  | Signature |  |  |
|  |  |  | Date |  |  |

# Existing Pressure System Details

|  |  |  |  | Design Approver Check Box |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| PSSR Reference Number |  |  |  |  |  |  |  |
| Pipeline Name |  |  |  |  |  |  |  |
| Pipeline Diameter |  | mm |  |  |  |  |  |
| Wall thickness |  | mm |  |  |  |  |  |
| Material Grade |  |  |  |  |  |  |  |
| Design Pressure |  | Barg |  |  |  |  |  |
| Maximum Operating Pressure (MOP) |  | Barg |  |  |  |  |  |
| Safe Operating Limit (SOL) |  | Barg |  |  |  |  |  |
| Hydrostatic Test Pressure |  | Barg |  |  |  |  |  |
| Design Factor |  | % SMYS |  |  |  |  |  |
| Building Proximity Distance (minimum) |  | metres |  |  |  |  |  |
| Non-Destructive Testing (NDT) on existing welds | Type | Tick as Applicable |  |  |  |  |  |
|  | 10% |  |  |  |  |  |  |
|  | 100% |  |  |  |  |  |  |
|  | Gamma |  |  |  |  |  |  |
|  | X-Ray |  |  |  |  |  |  |
|  | Design Approver Name |  |  |  |  |  |  |
|  | Signature |  |  |  |  |  |  |
|  | Date |  |  |  |  |  |  |

# Design Specifications

## Pressure Reduction Installations (Inlet Pressures up to 100 Bar)

| Pressure Reduction Installations Sheet 1 of 4 |  | Tick where Applicable | Design Approver Check Box |
| --- | --- | --- | --- |
| PSSR Ref |  |  |  |
| Station name |  |  |  |
| Station Design Parameters |  |  |  |
| Inlet Pressure (maximum) |  | Barg |  |
| Inlet Pressure (minimum) |  | Barg |  |
| Outlet Pressure (maximum) |  | Barg |  |
| Outlet Pressure (minimum) |  | Barg |  |
| Flowrate (maximum) |  | SCMH |  |
| Flowrate (minimum) |  | SCMH |  |
| Minimum Effective Downstream Volume |  | M3 |  |
| Inlet Gas Temperature |  | Deg C |  |
| Required Outlet Gas Temperature |  | Deg C |  |
| State any Pressure/Flow conditions which occur simultaneously:- |  |  |  |
| Inlet Design Pressure |  | Barg |  |
| Outlet Design Pressure |  | Barg |  |
| Inlet Maximum Operating Pressure (MOP) |  | Barg |  |
| Outlet Maximum Operating Pressure (MOP) |  | Barg |  |
|  | Design Approver Name |  |  |
|  | Signature |  |  |
|  | Date |  |  |

| Pressure Reduction Installations Sheet 2 of 4 |  | Tick where Applicable | Design Approver Check Box |
| --- | --- | --- | --- |
| Inlet Safe Operating Limit (SOL) |  | Barg |  |
| Outlet Safe Operating Limit (SOL) |  | Barg |  |
| Class Rating of Equipment and Fittings | Class 600 |  |  |
|  | Class 300 |  |  |
|  | Class 150 |  |  |
| Design Code(s) | IGEM/TD/1 |  |  |
|  | IGEM/TD/12 |  |  |
|  | IGEM/TD/13 |  |  |
| Others - (Please Specify) |  |  |  |
| Equipment Specifications |  |  |  |
| Valves | SGN/S/PV/6: Part 1 |  |  |
|  | SGN/SPV/6: Part 2 |  |  |
|  | SGN/SPV/8 |  |  |
|  | GIS/V7 |  |  |
| Waterbath Heaters | SGN/SP/E/7 |  |  |
| Filters | SGN/SP/E/13 |  |  |
| Insulating Joints | SGN/SP/E/56 |  |  |
| Specification for Pressure Resuction Installations 7 - 100 bar | SGN/SP/E/28 |  |  |
| Specification for Small Offtakes 7 – 49 bar | SGN/SP/E/33 |  |  |
| Valve Actuators | SGN/SP/VA/1 |  |  |
|  | SGN/SP/VA/2 |  |  |
| Pressure Gauges | SGN/SP/INP/3 |  |  |
|  | Design Approver Name |  |  |
|  | Signature |  |  |
|  | Date |  |  |

| Pressure Reduction Installations Sheet 3 of 4 |  | Tick where Applicable | Design Approver Check Box |
| --- | --- | --- | --- |
| Material Specifications |  |  |  |
| Pipe | TS-C4Gas-PIPO |  |  |
|  | GIS/L2 |  |  |
| Stainless Steel Impulse Pipe | ASTM A269 GR.316 |  |  |
| Forged Bends | SGN/SP/B/12 & SGN/SP/MPQ/2 |  |  |
| Forged Tees | SGN/SP/B/12 & SGN/SP/MPQ/2 |  |  |
| Reducers | SGN/SP/B/12 & SGN/SP/MPQ/2 |  |  |
| End caps | SGN/SP/B/12 & SGN/SP/MPQ/2 |  |  |
| Flanges | SGN/SPF/1 |  |  |
|  | GIS/F7 |  |  |
|  | BS EN 1092 |  |  |
| Weldolets | SGN/SPF/1 |  |  |
| Fittings | BS 3799 |  |  |
| Stainless Steel Compression Fittings | GIS/F9 |  |  |
| Others - (Please Specify) |  |  |  |
| Construction Specifications |  |  |  |
| Specification for Pipework Systems | SGN/SP/PW/11 |  |  |
| Auxiliary Services Pipework | SGN/SP/PW/6 |  |  |
| Welding | SGN/SP/P/2 |  |  |
| Testing | SGN/WI/PT/1 |  |  |
| Safety | SGN/PR/SSW/2 |  |  |
| Hazardous Area Classification | IGEM/SR/25 |  |  |
|  | Design Approver Name |  |  |
|  | Signature |  |  |
|  | Date |  |  |

| Pressure Reduction Installations Sheet 4 of 4 |  | Tick where Applicable | Design Approver Check Box |
| --- | --- | --- | --- |
| Noise | SGN/PM/SHE/05 |  |  |
| Jointing | SGN/SP/E/55 |  |  |
| Pipe Threads for Pipes and Fittings | SGN/SP/E/55 |  |  |
| Washers | SGN/SP/E/55 |  |  |
| Studbolts and Gasket Ring Data | SGN/SP/E/55 |  |  |
| Insulated Flanges | SGN/SP/E/56 |  |  |
| Corrosion Protection | SGN/PM/ECP/2 |  |  |
| Security Fencing | SGN/SP/CE/9 |  |  |
| Acoustic Insulation | SGN/SP/PWC/1 |  |  |
| Thermal Insulation | SGN/SP/PWC/2 |  |  |
| Wrapping | SGN/SP/CW/5 |  |  |
| Handrail Structures and Platforms | SGN/SP/SHR/1 |  |  |
| Painting | SGN/SP/PA/10 |  |  |
| Others - (Please Specify) |  |  |  |
| Data Sheets |  |  |  |
| Steel Pipework | SGN/SP/DAT/6 |  |  |
| Small Bore Steel Pipe | SGN/SP/DAT/6 |  |  |
|  | Design Approver Name |  |  |
|  | Signature |  |  |
|  | Date |  |  |

## < 7 Bar Steel System

| < 7 Bar Steel System Sheet 1 of 4 |  |  |  | Design Approver Check Box |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| PSSR Ref |  |  |  |  |  |  |
| Pipeline Name |  |  |  |  |  |  |
| Pipeline Diameter |  | mm |  |  |  |  |
| Wall thickness |  | mm |  |  |  |  |
| Material Grade |  |  |  |  |  |  |
| Design Pressure |  | Barg |  |  |  |  |
| Maximum Operating Pressure (MOP) |  | Barg |  |  |  |  |
| Safe Operating Limit (SOL) |  | Barg |  |  |  |  |
| Design Factor |  | % SMYS |  |  |  |  |
| Building Proximity Distance (minimum) |  | metres |  |  |  |  |
|  | Design Approver Name |  |  |  |  |  |
|  | Signature |  |  |  |  |  |
|  | Date |  |  |  |  |  |

| < 7 Bar Steel System Sheet 2 of 4 |  | Tick where Applicable | Design Approver Check Box |
| --- | --- | --- | --- |
| Design Code(s) | IGEM/TD/3 |  |  |
|  | IGEM/TD/4 |  |  |
|  | IGEM/TD/12 |  |  |
|  | IGEM/GL/1 |  |  |
| Others - (Please Specify) |  |  |  |
| Equipment Specifications |  |  |  |
| Valves | GIS/V7 Part 1 |  |  |
| Insulating Joints | GIS/E17: Part 2 |  |  |
| Valve Actuators | SGN/SP/VA/1 |  |  |
|  | SGN/SP/VA/2 |  |  |
| Pressure Gauges | SGN/SP/INP/3 |  |  |
| Others - (Please Specify) |  |  |  |
| Material Specifications |  |  |  |
| Pipe | TS-C4Gas-PIPO |  |  |
| Stainless Steel Impulse Pipe | ASTM A269 GR.316 |  |  |
| Forged Bends | GIS/F7 |  |  |
| Flanges | GIS/F7 |  |  |
|  | BS EN 1092 |  |  |
| Weldolets | GIS/F7 |  |  |
| Reducers | GIS/F7 |  |  |
| Forged Tees | GIS/F7 |  |  |
| Stainless Steel Compression Fittings | GIS/F9 |  |  |
| Others - (Please Specify) |  |  |  |
|  | Design Approver Name |  |  |
|  | Signature |  |  |
|  | Date |  |  |

| < 7 Bar Steel System Sheet 3 of 4 |  | Tick where Applicable | Design Approver Check Box |
| --- | --- | --- | --- |
| Construction Specifications |  |  |  |
| SGN Engineering Procedures |  |  |  |
| Excavation and Reinstatement | SGN/PM/MSL/1 |  |  |
| Pipe System Construction | SGN/PM/MSL/1 |  |  |
| Testing | SGN/PM/MSL/1 |  |  |
| Commissioning | SGN/PM/MSL/1 |  |  |
| Under Pressure Working | SGN/PM/MSL/1 |  |  |
| Pipe System Construction (Services) | SGN/PM/MSL/1 |  |  |
| Welding | SGN/SP/P/1 |  |  |
|  | SGN/SPP/9 |  |  |
| Safety | SGN/PR/SSW/2 SGN/SP/SSW/22 GDN/SCO/1,2,4 & 5 SGN/PM/DP/1 |  |  |
| Hazardous Area Classification | IGEM/SR/25 |  |  |
| Noise | SGN/PM/SHE/05 |  |  |
| Corrosion Protection | SGN/PM/ECP/2 |  |  |
| Acoustic Insulation | SGN/SP/PWC1 |  |  |
| Wrapping | SGN/SP/CW/5 |  |  |
| Handrail Structures and Platforms | SGN/SP/SHR/1 |  |  |
| Internal Coatings of Small Bore Pipe | SGN//SP/CM/2 |  |  |
| Painting | SGNPA/10 |  |  |
| Others - (Please Specify) |  |  |  |
|  | Design Approver Name |  |  |
|  | Signature |  |  |
|  | Date |  |  |

| < 7 Bar Steel System Sheet 4 of 4 |  |  |  | Tick where Applicable | Design Approver Check Box |
| --- | --- | --- | --- | --- | --- |
| Data Sheets |  |  |  |  |  |
| Pipe Threads for Pipes and Fittings |  | SGN/SP/E/55 |  |  |  |
| Steel Pipework |  | SGN/SP/DAT/6 |  |  |  |
| Jointing |  | SGN/SP/E/55 |  |  |  |
| Washers |  | SGN/SP/E/55 |  |  |  |
| Studbolts and Gasket Ring Data |  | SGN/SP/E/55 |  |  |  |
| Small Bore Steel Pipe |  | SGN/SP/DAT/6 |  |  |  |
| Insulated Flanges |  | SGN/SP/E/56 |  |  |  |
| Engineering Instructions |  |  |  |  |  |
| Hot Tap Connections |  | SGN/PM/MSL/1 |  |  |  |
| Pressure Testing Small Volume Systems |  | SGN/PM/MSL/1 |  |  |  |
|  | Design Approver Name |  |  |  |  |
|  | Signature |  |  |  |  |
|  | Date |  |  |  |  |

## < 7 Bar Plastic System

| < 7 Bar Plastic System Sheet 1 of 3 |  |  |  |  | Design Approver Check Box |  |
| --- | --- | --- | --- | --- | --- | --- |
| PSSR Ref |  |  |  |  |  |  |
| Pipeline Name |  |  |  |  |  |  |
| Pipeline Diameter |  | mm |  |  |  |  |
| Wall thickness |  | mm |  |  |  |  |
| Material Grade |  |  |  |  |  |  |
| Design Pressure |  | Barg |  |  |  |  |
| Maximum Operating Pressure (MOP) |  | Barg |  |  |  |  |
| Safe Operating Limit (SOL) |  | Barg |  |  |  |  |
| Design Factor |  | % SMYS |  |  |  |  |
| Building Proximity Distance |  | metres |  |  |  |  |
|  | Design Approver Name |  |  |  |  |  |
|  | Signature |  |  |  |  |  |
|  | Date |  |  |  |  |  |

| < 7 Bar Plastic System Sheet 2 of 3 |  |  |  | Tick where Applicable | Design Approver Check Box |
| --- | --- | --- | --- | --- | --- |
| Design Code(s) |  | IGEM/TD/3 |  |  |  |
|  |  | IGEM/TD/4 |  |  |  |
|  |  | IGEM/TD/12 |  |  |  |
|  |  | IGEM/GL/1 |  |  |  |
| PE80/100 |  | SGN/PM/MSL/1 |  |  |  |
| Others - (Please Specify) |  |  |  |  |  |
| Equipment Specifications |  |  |  |  |  |
| PE Installation Equipment |  | GIS/PL2 parts 3,5,7 |  |  |  |
| Valves |  | GIS/V7-1 GIS/V7- 2 |  |  |  |
| Others - (Please Specify) |  |  |  |  |  |
| Material Specifications |  |  |  |  |  |
| Pipe |  | GIS/PL2 part 2 (5.5 bar) GIS/PL2 part 8 (7 bar) |  |  |  |
| Flanges |  | GIS/F7 |  |  |  |
|  |  | BS EN 1092 |  |  |  |
| PE Fittings |  | GIS/PL2 parts 4 (class b) GIS/PL2 parts 6 (class c) |  |  |  |
| Others – (Please Specify) |  |  |  |  |  |
| Construction Specifications |  |  |  |  |  |
| SGN Engineering Procedures |  |  |  |  |  |
| Excavation and Reinstatement |  | SGN/PM/MSL/1 |  |  |  |
| Pipe System Construction PE80/100 |  | SGN/PM/MSL/1 |  |  |  |
| Testing |  | SGN/PM/MSL/1 |  |  |  |
| Commissioning |  | SGN/PM/MSL/1 |  |  |  |
| Under Pressure Working |  | SGN/PM/MSL/1 |  |  |  |
| Mains Insertion |  | SGN/PM/MSL/1 |  |  |  |
|  | Design Approver Name |  |  |  |  |
|  | Signature |  |  |  |  |
|  | Date |  |  |  |  |

| < 7 Bar Plastic System Sheet 3 of 3 |  |  |  | Tick where Applicable | Design Approver Check Box |
| --- | --- | --- | --- | --- | --- |
| Construction Specifications (continued) |  |  |  |  |  |
| SGN Engineering Procedures |  |  |  |  |  |
| Excavation and Reinstatement |  | SGN/PM/MSL/1 |  |  |  |
| Pipe System Construction PE80/100 |  | SGN/PM/MSL/1 |  |  |  |
| Testing |  | SGN/PM/MSL/1 |  |  |  |
| Commissioning |  | SGN/PM/MSL/1 |  |  |  |
| Under Pressure Working |  | SGN/PM/MSL/1 |  |  |  |
| Mains Insertion |  | SGN/PM/MSL/1 |  |  |  |
| Pipe System Construction (Services) |  | SGN/PM/MSL/1 |  |  |  |
| Pipe Lining Procedure |  | SGN/PM/MSL/1 |  |  |  |
| Moling Operations |  | SGN/PM/MSL/1 |  |  |  |
| Safety |  | SGN/PR/SSW/2 SGN/SP/SSW/22 GDN/MP/SCO 1,2,4 & 5 SGN/PM/DP/1 |  |  |  |
| Hazardous Area Classification |  | IGEM/SR/25 |  |  |  |
| Noise |  | SGN/PM/SHE/05 |  |  |  |
| Corrosion Protection |  | SGN/PM/ECP/2 |  |  |  |
| Wrapping |  | SGN/SP/CW/5 |  |  |  |
| Handling & Storage |  | IGEM/TD/1 Supplement 1 |  |  |  |
| Pipe Threads for Pipes and Fittings |  | SGN/SP/E/55 |  |  |  |
| Jointing |  | SGN/SP/E/55 |  |  |  |
| Washers |  | SGN/SP/E/55 |  |  |  |
| Studbolts and Gasket Ring Data |  | SGN/SP/E/55 |  |  |  |
| Insulated Flanges |  | SGN/SP/E/56 |  |  |  |
| Engineering Instruction |  |  |  |  |  |
| Maintenance , Connection & Repairs to PE Pipeline Systems |  | SGN/PM/MSL/1 |  |  |  |
| Others - (Please Specify) |  |  |  |  |  |
| Data Sheets |  |  |  |  |  |
|  | Design Approver Name |  |  |  |  |
|  | Signature |  |  |  |  |
|  | Date |  |  |  |  |

## 75 mBar – 100 Bar Metering Installation

| 75 mBar – 100 Bar Metering Installation Sheet 1 of 3 |  | Tick where Applicable | Design Approver Check Box |
| --- | --- | --- | --- |
| Design Code(s) | IGEM/TD/1 |  |  |
|  | IGEM/TD/12 |  |  |
|  | IGEM/TD/13 |  |  |
|  | IGEM/GM/8 |  |  |
| Others - (Please Specify) |  |  |  |
| Equipment Specifications |  |  |  |
| Valves | SGN/SP/V/6: Part 1 |  |  |
|  | SGN/SP/V/6: Part 2 |  |  |
|  | SGN/SP/V/8 |  |  |
|  | GIS/V7 |  |  |
| Meters | SGNSP/M/6 |  |  |
|  | SGN/SP/M/7 |  |  |
|  | SGN/SP/M/9 |  |  |
| Pressure Gauges | SGN/SP/INP/3 |  |  |
| Others - (Please Specify) |  |  |  |
| Material Specifications |  |  |  |
| Pipe | TS-C4Gas-PIPO |  |  |
|  | GIS/L2 |  |  |
| Stainless Steel Impulse Pipe | ASTM A269 GR.316 |  |  |
| Forged Bends | SGN/SP/B/12 & SGN/SP/MPQ/2 |  |  |
|  | Design Approver Name |  |  |
|  | Signature |  |  |
|  | Date |  |  |

| 75 mBar – 100 Bar Metering Installation Sheet 2 of 3 |  | Tick where Applicable | Design Approver Check Box |
| --- | --- | --- | --- |
| Flanges | SGN/SPF/1 |  |  |
|  | GIS/F7 |  |  |
|  | BS EN 1092 |  |  |
| Weldolets | SGN/SP/F/1 |  |  |
| Reducers | SGN/SP/B/12 & SGN/SP/MPQ/2 |  |  |
|  | GIS/F7 |  |  |
| Forged Tees | SGN/SP/B/12 & SGN/SP/MPQ/2 |  |  |
| Fittings | BS: 3799 |  |  |
| Stainless Steel Compression Fittings | GIS/F9 |  |  |
| Others - (Please Specify) |  |  |  |
| Construction Specifications |  |  |  |
| Specification for Pipework Systems | SGN/SP/PW/11 |  |  |
| Auxiliary Services Pipework | SGN/SP/PW/6 |  |  |
| Welding | SGN/SP/P/2 |  |  |
| Testing | SGN/WI/PT/1 |  |  |
| Safety | SGN/PRSSW/2 |  |  |
| Hazardous Area Classification | IGEM/SR/25 |  |  |
| Noise | SGN/PM/SHE/05 |  |  |
| Jointing | SGN/SP/PW/11 & SGN/SP/E/55 |  |  |
| Pipe Threads for Pipes and Fittings | SGN/SP/E/55 |  |  |
| Washers | SGN/SP/E/55 |  |  |
| Studbolts and Gasket Ring Data | SGN/SP/E/55 |  |  |
| Insulated Flanges | SGN/SP/E/56 |  |  |
| Corrosion Protection | SGN/PM/ECP/2 |  |  |
| Acoustic Insulation | SGN/SP/PWC/1 |  |  |
| Thermal Insulation | SGN/SP/PWC/2 |  |  |
| Wrapping | SGN/SP/CW/5 |  |  |
|  | Design Approver Name |  |  |
|  | Signature |  |  |
|  | Date |  |  |

| 75 mBar – 100 Bar Metering Installation Sheet 3 of 3 |  | Tick where Applicable | Design Approver Check Box |
| --- | --- | --- | --- |
| Handrail Structures and Platforms | SGN/SP/SHR/1 |  |  |
| Painting | SGN/SP/PA/10 |  |  |
| Others - (Please Specify) |  |  |  |
| Data Sheets |  |  |  |
| Steel Pipework | SGN/SP/DAT/6 |  |  |
| Small Bore Steel Pipe | SGN/SP/DAT/6 |  |  |
|  | Design Approver Name |  |  |
|  | Signature |  |  |
|  | Date |  |  |

## Cathodic Protection

| General | ### Project Title |  |  |  |  |  |  |  |  |  |  |  | Project Number/Finance code |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Location / Address |  |  |  |  |  |  |  |  |  |  |  | Reference Number: |  |  |  |
| Installation | CP System Type: Impressed Current: |  |  |  |  |  |  | Valves Fitted |  |  |  |  | Installation Date: / / |  |  |  |
|  | Sacrificial Anodes: |  |  |  |  |  |  | Yes/No: |  |  |  |  | DRS Attached: Yes / No |  |  |  |
|  | Pipe |  | Diameter | Coating |  |  | Length | Valves Wrapped |  |  |  |  | Easting: |  |  |  |
|  | Details |  |  |  |  |  |  | Yes/No: |  |  |  |  | Northing: |  |  |  |
|  | CP Post |  | Numbers | Anode |  |  | Numbers |  |  |  | Groundbed, Transformer. |  |  |  | Coupons Fitted |  |
|  |  |  |  |  |  |  | per |  |  |  |  |  |  |  |  |  |
|  | Details |  |  | Details |  |  | CP Post |  |  |  | Installed: Yes/No |  |  |  | Yes/No: |  |
|  | Sleeve(s) |  | Installed | Sleeve location if yes |  |  |  | Sleeve construction details |  |  |  |  |  |  |  |  |
|  |  |  | Yes/No |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Installer: |  |  | Name |  |  |  | Signature |  |  |  |  |  |  | Date |  |
|  | Supervisor |  |  | Name |  |  |  | Signature |  |  |  |  |  |  | Date |  |
|  | Inspector |  |  | Name |  |  |  | Signature |  |  |  |  |  |  | Date |  |
| Commiss- ioning | Cathodic Protection Satisfactory |  |  |  |  |  |  |  | Yes | No |  |  |  |  |  |  |
|  | Inspectors comments: |  |  |  |  | ##### Tick applicable box/boxes |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | CP Satisfactory commissioned and entered into monitoring database. |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | CP Out with the levels required by T/PM/ECP.1 (actual reading…………..mVolts) |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | CP Cables not accessible for safety reasons or due to poor installation. |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Unable to Locate. |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Other |  |  |  |  |  |  |  |  |  |  |
|  | Suggestions as to remedial actions required: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Commissioned by: |  |  | Name |  |  |  | Signature |  |  |  |  |  |  | Date |  |
|  | Network Services |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | P.C. S Ref. No. / |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Any other comments/information: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | This form will required to be sent to Asset Engineering Manager for acceptance and for the P.C.S Ref. Number to be applied. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The original form with all the appropriate signatures must be included in the completed project folder. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Design Approver Name |  |
| --- | --- |
| Signature |  |
| Date |  |

## Civil Works

|  |  |  |  | Tick where Applicable |  | Design Approver Check Box |
| --- | --- | --- | --- | --- | --- | --- |
| Design Codes and Material Specifications |  |  |  |  |  |  |
| Site Investigations |  | BS: 1377 |  |  |  |  |
|  |  | BS: 5930 |  |  |  |  |
| Loading | Dead | BS: 648 |  |  |  |  |
|  |  | BS: EN 1991 |  |  |  |  |
|  | Wind | BS: EN 1993 |  |  |  |  |
|  |  | BS: EN 1991 |  |  |  |  |
|  |  | BS: EN 40 |  |  |  |  |
|  |  | BS: EN 1991 |  |  |  |  |
| Foundations |  | BS: EN 1997 |  |  |  |  |
| Earthworks |  | BS: 6031 |  |  |  |  |
| Earth Retaining Structures |  | BS: EN 1997 |  |  |  |  |
|  |  | BS: EN 1992 |  |  |  |  |
|  |  | BS: 8500 |  |  |  |  |
| Steelwork |  | BS: EN 1994 |  |  |  |  |
|  |  | BS: EN 1993 |  |  |  |  |
| Masonry |  | BS: EN 1996 |  |  |  |  |
| Timber |  | BS: 5268 |  |  |  |  |
| Drainage |  | BS EN: 752 |  |  |  |  |
| Stairs, Ladders and Walkways |  | SGN/SP/SHR/1 |  |  |  |  |
|  |  | BS: 5395 |  |  |  |  |
| Acoustic Enclosures |  | SGN/SP/E/25 |  |  |  |  |
| Specification for Earthing |  | SGN/SP/EL/13 |  |  |  |  |
| Housings for Governor Installations |  | SGN/SP/E/28 |  |  |  |  |
| Fencing - Chain Link 2.4m Steel Posts |  | SGN/SP/CE/9 |  |  |  |  |
|  |  | BS: 1722 |  |  |  |  |
| Fencing - Chain Link 2.4m Concrete Posts |  | SGN/SP/CE/9 |  |  |  |  |
|  |  | BS: 1722 |  |  |  |  |
| Fencing - Palisade | 2.4m | SGN/SP/CE/9 |  |  |  |  |
|  |  | BS: 1722 |  |  |  |  |
|  | 3m | SGN/SP/CE/9 |  |  |  |  |
|  |  | BS: 1722 |  |  |  |  |
| Others - (Please Specify) |  |  |  |  |  |  |
|  | Design Approver Name |  |  |  |  |  |
|  | Signature |  |  |  |  |  |
|  | Date |  |  |  |  |  |

# Other items which Appraisals will check

## Mechanical / Gas Process Engineering Appraisal

SHEET 1 of 4

| A/B/C |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMMENTS | Pressures, temperatures, flows and combinations thereof Safe Operating Limits, design pressures, test pressures Planning Data Sheet Fatigue data Velocities Gas Composition | Material schedule provided giving all details Sizing criteria Operation/performance including noise level predictions Equipment/materials data sheets Equipment pressure rating Reference to relevant SGN specification Manufacturer/contractor calculations Equipment operating mode Design factor checks Pipe/fittings material, grade, wall thickness | Method of overpressure protection Dynamics/Transients – Network Study report Security of supply, reliability Derivation of control philosophy ELD Derivation of equipment set-points | Structural calculations & assumptions, static/dynamic loading Design code | Pressure test drawing – main & auxiliary pipework Consideration of water fill & drainage Hot tap fitting test Test levels & duration including elevation criteria Design code e.g, ANSI 31.8 etc |
| OPERATION | Design conditions | Equipment & materials rating & specifications | Control philosophy, overpressure protection | Pipe supports, anchors & guides | Pressure testing |
| ITEM | 1 | 2 | 3 | 4 | 5 |

SHEET 2 of 4

| A/B/C |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| COMMENTS | Interface codes e.g. IGEM TD/12, ANSI 31.3 etc Derivation of load cases Materials & geometry data Pressure stiffening effects Pipe supports, anchors & settlement Design life & cycling requirements Review of output data Finite Element analysis of code exceptions | Specialist activity – refer to CP engineer – consider pressure rating of equipment | SHA1SR25 drawings & calculations – plan & elevations Derivation of zoning data Compliance with procedures Maintenance interval considerations Overlapping of zones Manual venting - SGV2 | List of appropriate SGN codes Non- SGN codes Interface between codes | HAZOP/HAZID/HAZCON Report | Design codes Velocity calculations Pressure drop calculations | Sizing calculations, operating philosophy Pressure vessel codes Pressure drop calculations |
| OPERATION | Pipework Stress Analysis | Cathodic Protection | Hazardous areas | Construction design codes & standards | Design Risk Assessments | Pipework sizing | Filtration |
| ITEM | 6 | 7 | 8 | 9 | 10 | 11 | 12 |

SHEET 3 of 4

| A/B/C |  |  |  |  |
| --- | --- | --- | --- | --- |
| COMMENT | Sizing calculations Pipework configuration – upstream/ downstream diameters ratio etc Manufacturer’s design data – turndown etc | Design code/specification Heat requirement & heat exchanger sizing calculations Pre-heat system (waterbath, heat exchanger, vortex etc) Pressure vessel codes Overpressure protection Hot water system sizing calculations Auxiliary pipework sizing & specifications Predicted noise emissions Manufacturer’s design data | Regulator/recycle valve capacity calculations Operating philosophy Full fault capacity Pressure relief valve sizing Derivation of set points Manufacturer’s design data Predicted noise emissions | Specialist activity – refer to Compressor specialist |
| OPERATION | Metering | Pre-heating | Pressure & flow control | Rotating machinery |
| ITEM | 13 | 14 | 15 | 16 |

SHEET 4 of 4

| A/B/C |  |  |  |
| --- | --- | --- | --- |
| COMMENT | Establishment of Building Proximity Distances IGEM/TD/1, IGEM/TD/2 and IGEM/TD/3 Population Density Survey Design factors Area Classification Environmental constraints Special crossings Sensitive locations Risk assessments Block valves On-line inspection requirements Under-pressure connections Pressure testing Unstable ground Uprating/MPOP restoration Commissioning Construction & access Proximity to other services | CDM requirements Operation Maintenance Decommissioning Demolition | All equipment (mechanical & electrical) specified for use in a hazardous area should be selected in accordance with the DSEAR regulations. Hazardous area zoning Equipment selection suitable for zone / risk assessment Signage of hazardous area (EB18) BS EN 60079 series |
| OPERATION | Pipelines Routing | Overall safety considerations applicable to all disciplines and asset categories | ATEX / DSEAR |
| ITEM | 17 | 18 | 19 |

## Civil / Structural Appraisal

SHEET 1 of 5

For Appraisals of Civil/Structural designs the following should be considered

- All loading that the system may be subjected to. (dead, imposed, wind, snow, ice, earth, water, dynamic, thermal, vibration, friction, impact, fire, hydro test, etc.).

- Materials behaviour (e.g. shrinkage, provision of movement joints etc.) and timing of loading (e.g. concrete strength at application of load).

- The effects of any possible ground movement (settlement, shrinkage, swelling and any changes in ground water levels etc.).

- The results of site investigations (boreholes, trial pits, water levels and results of analysis, etc.) or previous borehole records. If these have not been provided or the investigation has been of a limited extent the implications of this must be considered. If the implications may affect the system the appraiser should either request additional information or ensure that the necessary qualifications are included in the signed appraisal.

- Geotechnical interpretation and analysis.

- Effect of the installation on the local topography, ground conditions and existing adjacent structures and the effect of the local topography or adjacent structures on the installation, e.g. slope stability, undermining of existing structures, mining subsidence, road, railway or waterway.

- Stress analysis including details of how restraints and/or supports were modelled, the derivation of soil restraint values and/or soil loadings and table of loadings at supports and/or restraints for all load cases.

- Foundation and substructure design.

- Superstructure design including pipe supports, access ladders and platforms, etc.

- Equipment housing and covers.

- Roads and drainage layout and details where such may affect the integrity and performance of the pressure system.

- Security details including fences, crash barriers and bollards.

- List of standards and design references used.

- Testing parameters and regimes for materials and workmanship.

SHEET 2 of 5

Notes for completion of Appraisal Checklist - Civil & Structural Engineering

The Appraisal Checklist is to be completed by the Appraiser at the commencement of the process.

All sections will be completed by the Appraiser in black ink and will become part of the documentation submitted to SGN.

The first sheet (1-33) will be completed for the site and the second sheet (A1-A25) will be completed for each structure or set of structures.

1-4 All drawings and calculations should be signed as checked and approved. Appraiser to ascertain that the persons signing are approved by SGN for the role.

5 Appraiser should ensure that all Standards and Design References used are included in the list and that they are appropriate.

6-10 Ensure that Material and Workmanship Specifications include the necessary information to obtain and use the correct materials and include the correct and current codes.

10 Insert any other materials that require specifications for the project.

11 Peripheral site information may include topography, rivers, coast, buildings, roads, railways etc. where it may have an effect on the pressure system.

12 Have all the effects of 11 been considered by the designer?

13 Has the designer considered the effects of existing structures and how they may affect the pressure system?

14 Have the effects of past or future mining and tunnelling been considered by the designer and how they may affect the pressure system?

15 Have the effects of earthquakes as outlined in IGEM/TD/12 been considered?

16 An adequate Site Investigation could consist of boreholes or trial pits, including site and laboratory tests to establish the underlying ground conditions including analysis and interpretation. The extent will depend on the site being considered and the nature of the structure to be constructed on the site. The designer must have demonstrated that all of the above have been considered and that sufficient information has been obtained to allow confidence in the design.

17 If no Site Investigation has been carried out the designer must demonstrate where the basis of information has been obtained from and how he has reached his conclusions.

18, 19 Has the designer demonstrated whether any piling or ground improvement has been required and full details provided?

20-22 Has the designer considered the effects of ground movement on the structures on site?

23-27 Stress Analysis.

28 Will any existing or proposed roads affect the integrity of the pressure system?

29 Will any existing or proposed drainage, culverts, sewers affect the pressure system?

SHEET 3 of 5

30 Have the requirements for fences, crash barriers and bollards been considered and are the considered to be adequate?

31 The appraiser must satisfy himself that all design considerations that may affect the integrity of the pressure system have been considered.

32 Has the designer identified any deviations from Policies, Procedures, Specifications and Engineering Instructions and informed the Project Coordinator of the fact, and the necessary Procedure for the Technical Assessment of Deviations and Concessions has been followed?

A1 Appraiser to fill in the name of the structure or series of structures being appraised.

A2 -15 Has the correct condition and combination of loading been considered and have the correct British or SGN Standards been used and correctly applied?

A16 - 25 Have the necessary drawings and calculations been provided to carry out the appraisal?

SHEET 4 of 5

| COMMENTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| OPERATION | Has a Design Brief been provided? | Have all drawings been checked? | Have all drawings been approved? | Have all calculations been checked? | Have all calculations been approved? | Has an adequate list of Design Standards and Design References been provided? | Concrete? | Steel? | Backfill /Replacement material? | Timber? | Other? | Has adequate peripheral site information been provided? | Have all the effects of peripheral sites been considered? | Have the effects of any existing structures on site been considered? | Have the effects of mining/tunnelling been considered? | Have the effects of earthquakes been considered? | Has an adequate Site Investigation been carried out and full report provided? | If no SI, have Soil Conditions been established? | Drawings provided? | Calculations, method statements provided? | Settlement? | Shrinkage? | Swelling? | Has Stress Analysis been provided? | Have sufficient and correct load cases been provided? | Has the method of modelling of restraints/supports been provided? | Derivation of Soil Restraint Values provided? | Table of Loadings at Supports/Restraints provided for all load cases? | Will road layout or structural design affect the integrity of the system? | Will drainage layout or structural design affect the integrity of the system? | Are security details (fences, crash barriers/bollards) adequate? | Have all design conditions that may affect the pressure system been considered? | Have any Deviations from Policies, Procedures, Specifications and Engineering Instructions been identified? |
|  |  |  |  |  |  |  | Adequate Material and Workmanship Specifications provided? |  |  |  |  |  |  |  |  |  |  |  | Piling, ground improvement required? |  | Has ground movement been considered? |  |  | Stress Analysis |  |  |  |  |  |  |  |  |  |
| ITEM | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 |

SHEET 5 of 5

| COMMENTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| OPERATION |  |  | Dead? | Imposed? | Wind? | Snow? | Ice? | Earth? | Water? | Dynamic? | Thermal? | Vibration? | Friction? | Impact? | Hydro test? | Fire? | Drawings provided? | Calculations provided? | Drawings provided? | Calculations provided? | Drawings provided? | Calculations provided? | Details provided? | Ventilation calculations provided? | Explosion relief calculations provided? | Overall stability calculations provided? |
|  |  | Structure being appraised? | Loading Considered? |  |  |  |  |  |  |  |  |  |  |  |  |  | Foundation and substructure |  | Superstructure |  | Pipe support |  | Equipment Housings |  |  |  |
| ITEM | A1 |  | A2 | A3 | A4 | A5 | A6 | A7 | A8 | A9 | A10 | A11 | A12 | A13 | A14 | A15 | A16 | A17 | A18 | A19 | A20 | A21 | A22 | A23 | A24 | A25 |

## Safety / Human Factors Appraisal

The Appraiser needs to check for the following documents, tabulated below. Key documents for all projects or modifications are shown in bold.

| ALL |  | CONCEPTUAL | DETAILED |
| --- | --- | --- | --- |
| Site Selection |  | Assessment |  |
| Environment |  | Impact Assessment | Applications |
|  |  | Discharge consent |  |
| Planning |  | Application required | Applications |
|  |  | Consent required |  |
| Reliability |  | User requirements |  |
| HSE guidance |  | Use of relevant guides |  |
| Safety Recommendations / Design Codes |  | Use of relevant recommendations & codes |  |
| Health and Safety File |  | Started | Register |
| Layout Review |  | Assessment report | Report |
| Venting options |  |  | Report |
| Hazardous Area Classification |  | Basis | Drawings/ Calculations |
| DSEAR/ATEX |  | Statement | Report / equip. register Risk Assessment |
| Safety Issues |  | Start register | Register - any relevant Risk Assessments |
| Emergency Procedures |  |  | Update |
| Notifications |  | Required | Application |

## Cathodic Protection Appraisals

For Appraisals of Cathodic Protection designs the following should be considered.

- Proposed route, length, and diameter of pipework including offtakes, spurs, block valves, pigtraps, sleeves, ancillary equipment and proximity to other buried metallic plant.

- How the new scheme will fit into any existing cathodic protection system

- Liaison with other authorities, particularly identification of 3rd party CP systems.

- Factory and field applied coatings for buried pipework, including the need for specialist backfill and also any requirement for painting of above ground structures.

- Requirement for and location of insulation joints or flanges.

- Choice of system i.e. Sacrificial anode or Impressed current, including type and siting of groundbed and transformer/rectifier, positions of routine monitoring facilities, cable type and size, soil resistivities and avoidance of hazardous zones.

- Provision of specialist monitoring facilities i.e. coupons buried reference electrodes and resistance probes.

- Consider the need for mitigation and review such design.

- Supporting calculations.

- Special crossings i.e. overhead, river or canal and sleeved.

- Avoidance of contact with other buried metallic plant, reinforced concrete.

- Adverse interaction or CP current drainage to earthing system, consider also the significance of the earthing arrangements for remotely operated valves.

- CP commissioning, post construction surveys and interaction testing requirements.

- List of standards and design references used.

- Appraisers should assess the risk of AC corrosion on any new pipelines.

The above is not an exhaustive list. The Appraiser must use his/her knowledge and experience when undertaking the Appraisal.